## Slide 1
Ministry of Higher Education &scientific Research
Al-Mustansiriya University
College of Engineering
Energy management and applications
Insulations
Asst. Prof. Dr. Hayder Mohammad Jaffal
(Section 3)

## Slide 2
Insulation materials are extensively used to reduce the heat losses (or gains) from thermal systems like buildings, pipes and ducts, components of HVAC installations, etc. Most mass-type thermal insulation materials are highly porous, and consist of a solid matrix full of small voids that comprise 90% or more of the total volume. These voids contain air or some other harmless gas such as CO2. The apparent conductivity of the material is the macroscopic result of various basic heat transfer mechanisms: solid and gas conduction, gas convection and long-wave radiation within the voids. From the macroscopic point of view, the apparent conductivity mainly depends on the kind of insulation, bulk density, temperature, water content, thickness and age. From the microscopic point of view, factors such as cell size, diameter and arrangement of fibers or particles, transparency to thermal radiation or type and pressure of the gas come into play.
1- Introduction

## Slide 3
2- Purpose of Insulation
A thermal insulator is a poor conductor of heat and has a low thermal conductivity. Insulation is used in buildings and in manufacturing processes to prevent heat loss or heat gain. Although its primary purpose is an economic one, it also provides more accurate control of process temperatures and protection of personnel. It prevents condensation on cold surfaces and the resulting corrosion. Such materials are porous, containing large number of dormant air cells. Thermal insulation delivers the following benefits:
1-Reduces over-all energy consumption
2-Offers better process control by maintaining process temperature.
3-Prevents corrosion by keeping the exposed surface of a refrigerated system above dew point.

## Slide 4
4-Provides fire protection to equipment
5-Absorbs vibration

## Slide 5
3- Types and Application
The Insulation can be classified into three groups according to the temperature ranges for which they are used.
Low Temperature Insulations (up to 90 °C)
This range covers insulating materials for refrigerators, cold and hot water systems, storage tanks, etc. The commonly used materials are Cork, Wood, 85% magnesia, Mineral Fibers, Polyurethane and expanded Polystyrene, etc.
Mineral Fibers Wall Insulation

## Slide 6
Medium Temperature Insulations (90 – 325 °C)
Insulators in this range are used in low temperature, heating and steam raising equipment, steam lines, flue ducts etc. The types of materials used in this temperatures range include 85% Magnesia, Asbestos, Calcium Silicate and Mineral Fibers etc.
Polyurethane

## Slide 7
High Temperature Insulations (325 °C – above)
Typical uses of such materials are super heated steam system, oven dryer and furnaces etc. The most extensively used materials in this range are Asbestos, Calcium Silicate, Mineral Fibre, Mica and Vermiculite based insulation, Fireclay or Silica based insulation and Ceramic Fibre.
Expanded Polystyrene

## Slide 8
4- Insulation material
Insulation materials can also be classified into organic and inorganic types. Organic insulations are based on hydrocarbon polymers, which can be expanded to obtain high void structures
Example: Thermocol (Expanded Polystyrene) and Poly Urethane Form (PUF).
Inorganic insulation is based on Siliceous/Aluminous/Calcium materials in fibrous, granular or powder forms.
Example: Mineral wool, Calcium silicate etc.

## Slide 9
Calcium Silicate: Used in industrial process plant piping where high service temperature and compressive strength are needed. Temperature ranges varies from 40 °C to 950 °C.
Glass mineral wool: These are available in flexible forms, rigid slabs and preformed pipe work sections. Good for thermal and acoustic insulation for heating and chilling system pipelines. Temperature range of application is –10 to 500 °C.
Thermocol: These are mainly used as cold insulation for piping and cold storage construction.
Expanded nitrile rubber: This is a flexible material that forms a closed cell integral vapour barrier. Originally developed for condensation control in refrigeration pipe work and chilled water lines; now-a-days also used for ducting insulation for air conditioning.
Properties of common insulating materials are as under:

## Slide 10
Rock mineral wool: This is available in a range of forms from light weight rolled products to heavy rigid slabs including preformed pipe sections. In addition to good thermal insulation properties, it can also provide acoustic insulation and is fire retardant.

## Slide 11
Materials used in thermal insulation applications generally are grouped according to the temperature range in which they are employed. The temperatures that limit these ranges are somewhat arbitrary. When the temperature reaches an upper limit, materials may be damaged or become uneconomical because their thermal conductivity increases. A lower limit usually means that the material is not competitive because there are cheaper materials that can perform satisfactorily. Within each temperature range, the selection is made taking into consideration other properties and cost . The temperature range within which the term “thermal insulation” applies, is from73˚C to 982˚C. All applications below -73˚C are termed cryogenic and those above 982˚C are termed refractory.
5- Thermal insulation materials

## Slide 12
Thermal insulation of building walls has a significant effect on the reduction of thermal energy consumption in buildings that leads to the reduction of CO2 emissions. Making a thermal insulation of a building external wall can in terms of economic aspects be approached as an investment. In this investment the cost is related to the purchase, transport and laying the insulation, whereas the profits are linked to the reduction of thermal energy consumption necessary to heat a building. One of the most effective ways to do this is to reduce the energy consumption of buildings, which comprise approximately one-third of global energy consumption. In many previous studies, the application of thermal insulation to the external walls of a building was determined as the most effective means of reducing energy consumption.
6- Benefits of thermal insulation of building external walls

## Slide 13
The U-value is calculated by :
U =heat transfer coefficient (W/m² ̊ C)
Ri=internal heat transfer resistance (̊ C /W)
Ro=external heat transfer resistance (̊ C /W)
Rw= heat transfer resistance of wall layer without insulation (̊ C /W)
Rins=heat transfer resistance of the insulation (̊ C /W)
The thermal resistance of the insulation calculates as follows:
Δx=thickness of the insulation layer (m)
ki=thermal conductivity of the insulation layer (W/m ̊ C )

## Slide 14
Total resistance of the non-insulated wall layer Rw,t is:
Total building load coefficient (BLC) is expressed as:
For energy savings. The energy lost to the ambient needs to be supplied at the expense of a higher fuel or electricity consumption. In these cases, the cost of a higher insulation thickness must be economically balanced again the higher fuel consumption.

## Slide 15
By applying insulation to buildings’ external walls, heat loss and gain through the building surface is significantly reduced. However ,a cost analysis should be performed to determine the optimum insulation thickness. Annual energy cost for unit surface CA,h and CA,c are calculated with the following equation:

## Slide 16
CAh= annual heating energy cost ($)
CAc= annual cooling energy cost ($)
BLC=building load coefficient (W/ ̊ C)
HDDa= annual heating degree day ( ̊ C.day)
CDDa= annual cooling degree day ( ̊ C.day)
ηH= is the average efficiency of the heating system
ηc= is the average efficiency of the cooling system
Cfuel=is unit fuel price ($/m3) or ($/kg)
Hu= is the heating value of fuel (J/m3) or (J/kg)
Celect=is the cost of electricity ($/J)

## Slide 17
Example 1:
A residential building located in Karkok that has the following data:
Areas:
Floor area= 14x8=112 m²
Roof area =112 m²
Door area=6 m²
Window area=14 m²
Height=2.5 m
Walls =2x[14x2.5]+2[8x2.5]=110 m²
Wall area=Awall-[Awindow+Adoor]
=110-[14+6]=90 m²

## Slide 18
U-value:
Uwall=1.8 W/m² ̊ C
Uroof=1.2 W/m² ̊ C
Uwindow=6.7 W/m² ̊ C
Udoor=1.5 W/m² ̊ C
Foor:
The heat transfer coefficient for the floor is smaller than of walls and roof bearing in mind that the floor dos not expos to the outside condition. Therefore, ΔT is small and the thermal load is neglected.
Infiltration:
Use number of air change per hour (ACH=1.5)

## Slide 19
Express the effect of building material on the annual thermal load assume that 100 mm of insulation [k=0.036 W/ m ̊ C] is added to the roof. Giving that:
Tmax=34.9 ̊ C
Tmin=9.1 ̊ C
Qfree=3000 W for Summer
Qfree=2200 W for Winter
Ti=25 ̊ C for Summer
Tmin=22 ̊ C for Winter
Calculate the annual saving due to the addition of this material.

## Slide 20
Solution:

## Slide 21
Cooling before the addition :

## Slide 22
Heating before the addition :

## Slide 23
Total load without the insulation:
After the addition :

## Slide 25
Cooling after the addition :

## Slide 26
Heating after the addition :

## Slide 27
Total load with insulation :
The thermal load saving due to the addition of the insulation is :

## Slide 28
Example 2:
Calculate the energy saving due to the replacing the glass of windows for building ( located in USA) from single glazing double glazing. Give the following data:
Tmax=22.6 ̊ C
Tmin=-4 ̊ C
Ti=22.3 ̊ C for Summer
Tb=18. 3 ̊ C before changing the glass
Qfree=2000 W
Aglass=18.6 m²
Uglass=6.74 W/m² ̊ C ( single glazing )
Uglass=3.06 W/m² ̊ C (double glazing )

## Slide 29
Solution:
The total building load coefficient without windows is :

## Slide 30
The total building load coefficient with double glazing windows is :
Cooling :

## Slide 31
Heating :
For single glazing :
For double glazing :

## Slide 32
Total load with single glazing:
For single glazing :
For double glazing :
Total load with double glazing:

## Slide 33
The thermal load saving due use double glazing windows is :